Estt. Cost :- Rs. 21139800.00

Earnest Money Rs. 331272.00

Date of Sale 20.07.07

Date of Opening 07.08.07

SCHEDULE OF WORK

Name of work	:-	C/o 216 HIG DUs (Multistoreyed) i/c internal development at Pitampura near T.V. Tower Complex.

SH : Supplying and installation of lifts for 144 flats in group-II)

| S. NO. | Description of items | Qty. | Rate | Unit | Amount |
| --- | --- | --- | --- | --- | --- |
| 1. | Supplying, installation, testing, commissioning and putting into operation 8 passengers lift (544 kg.) with all accessories and control equipment for a total rise of 24 metres (approx.) (one way) with 9 landings/openings at a rated speed of 1.5 meters/second, as per detailed specification enclosed. | 4 nos. |  | Per lift |  |
| 2. | Supplying, installation, testing, commissioning and putting into operation 8 passengers lift (544 kg.) with all accessories and control equipments for a total rise of 30 metres (approx.) (one way) with 11 landings/openings at a rated speed of 1.5 meters/second, as per detailed specifications enclosed. | 4 Nos. |  | Per Lift |  |
| 3. | Comprehensive maintenance of 8 passengers with 9 landings/openings at a rated speed of 1.5 m/sec. lift which includes routine, preventive and break down maintenance for a period of five years including repair/replacement of worn out items, warranty and guarantee of repaired/replaced items after completion of one year guarantee period, as per additional terms and conditions enclosed. |  |  |  |  |
|  | a) 1st Year | 4 Nos. |  | Per Lift |  |
|  | b) 2nd year | 4 Nos. |  | Per Lift |  |
|  | c) 3rd Year | 4 Nos. |  | Per Lift |  |
|  | d) 4th Year | 4 Nos. |  | Per Lift |  |
|  | e) 5th Year | 4 Nos. |  | Per Lift |  |
| 4. | Comprehensive maintenance of 8 passengers with 11 landings/openings at a rated speed of 1.5 m/sec. lift which includes routine, preventive and break down maintenance for a period of five years including repair/replacement of worn out items, warranty and guarantee of repaired/replaced items after completion of one year guarantee period, as per additional terms and conditions enclosed. |  |  |  |  |
|  | a) 1st year | 4 Nos. |  | Per Lift |  |
|  | b) 2nd Year | 4 Nos. |  | Per lift |  |
|  | c) 3rd Year | 4 Nos. |  | Per Lift |  |
|  | d) 4th Year | 4 Nos. |  | Per lift |  |
|  | e) 5th Year | 4 Nos. |  | Per Lift |  |
|  |  |  | Total |  |  |

ADDITIONAL TERMS AND CONDITIONS

1.	GENERAL

1.1	The contractor must get acquainted with the proposed site for the work and study specifications & conditions carefully before tendering.  The work shall be executed in close coordination with the progress of building work.

1.2	The work, as indicated in the Schedule of work attached herewith including any modification/addition/alternation ordered subsequently shall be carried out in the following preference as per the specification indicated below:

i)	Indian Electricity rule 2005 amended upto date.

ii)	Delhi Lift Rules-1942

iii)	Relevant BIS standard as modified upto date.

iv)	Technical specifications attached herewith.

1.3	The safety provisions as per statutory regulations, BIS recommendations Regulations under Factories Act etc.  where applicable, and also instructions issued from time to time in respect of labour employed by the successful tenderer directly or indirectly for the installation of the lifts, shall be strictly followed.  Necessary barriers, warning signs and other safety measures wherever necessary to avoid accidents shall be provided.

In addition all safety procedures as outlined in Appendix VIII of general specifications for electrical works (part III lifts) 2003 shall be complied with.

1.4	SCOPE OF WORK:

The following shall be deemed to be included within the scope of work.

- All minor building work necessary for installation of equipment such as making of opening in walls/floors either RCC or brick masonry, and restoring them to original condition and finish.

- Supply of necessary R.S. Joists or angle iron supports/brackets etc. for installation of the lift, either in the machine room or at other places as may be necessary including their installation in position.

- All electrical works including inter-connection from TP&N switch and loop earthing from the earth bar provided in the machine room

- Responsibility to ensure safety of lift materials against pilferage & damage till the installation are handed over to the Department.

- All scaffolding work as may be necessary in the hoist way during erection and its subsequent removal.

- Temporary barricades with caution boards at each landing to prevent accident during the execution of work.

1.5	 WORKS TO BE ARRANGED BY DDA:

DDA shall be responsible for the following work only and these are excluded from the responsibility of the contractor:

a)	Provision of 3 phase 4 wire 50HZ 415 volts A.C. electric power supply terminated in the lift machine room with suitable size of TP&N switch for each lift.

b)	Provision of single phase 50Hz 230 volts A.C. power supply terminated with suitable size MCB for lighting inside the lift care.

c)	Free power for installation of lifts.

d)	Properly ventilated machine room, lift well and a water proof lift pit.

e)	Provision of adequate storage space for material.

f)	Provision of adequate lighting in the machine room, lift shaft and all landings.

g)	Provision of hoisting beam or hook above the lift well and trap door.

h)	Architrave work at lift entrance.

1.6	DRAWING AND DATA:

i)	The contractor shall furnish the following drawings and data to the Engineer-in-charge in triplicate, for approval within 15 days of award of work.

a)	General arrangement drawing

b)	Details of foundations for equipment, load data of various assembled equipments.  The data will include breaking load on guides, reactions on buffers, reaction on support in machine room, lift well etc.

c)	Dimensions for every unit and group of units for erection purpose, as required.

ii)	The correction/changes, if any, intimated by the Engineer-in-charge shall be incorporated and three sets of such corrected drawings shall be furnished to the Engineer-in-charge within 15 days from the date of approval of drawings.  The work shall be executed in accordance with the approved drawings.

1.7	SUPPLY OF MATERIAL:

Supply of material shall be phased in such a manner that erection work is not hampered for want of material	.  After award of work successful tenderer shall submit detailed programme bar chart for supply of material, erection, testing, commissioning and handing over of lifts.

1.8	QUALITY OF MATERIAL AND WORKMANSHIP:

All parts of the equipment shall be of such design, size and materials so as to function satisfactorily under all rated conditions of operation.  All components of the equipments shall have adequate factor of safety.  The work of fabrication and assembly shall confirm to sound engineering practice and on the basis of “Fail Safe Design”.  The mechanical parts subject to wear and tear shall be easily replaceable type.  The construction of the equipments shall be such as to facilitate easy operation, inspection, maintenance and repairs.  All connections and contacts shall be designed to minimize risk of accidental short circuits caused by animals, birds and vermin etc.  All identical items and their component parts should be completely, interchangeable including spare parts.

1.9	INSPECTION BEFORE DESPATCH:

All routine and type tests prescribed in relevant BIS specifications shall be conducted before dispatch of equipments.  No equipment shall be dispatched from the manufacturer’s premises without such tests being conducted and test result recorded.  These test certificates shall be given along with the supply of equipments.  The Engineer-in-charge shall, if he so desires inspect and witness the pre-delivery tests.  For this purpose, the contractor shall give 15 days advance information.  Department shall bear expenses for inspection as far as traveling and boarding/lodging is concerned.

  - INSPECTION AND TESTING AT SITE:

- The lift installation shall be subject to necessary inspection during every stage of erection by the Engineer-in-charge or his authorized representative.  The tenderer shall provide all facilities and assistance for the purpose.

- On completion of the installation, all adjustments as necessary shall be made for the satisfactory performance of the lifts.  The completed installation shall be inspected and tested by the Engineer-in-charge in the manner as will be laid down by him, in consultation with the contractor.  All tests necessary for satisfying the reliable performance of the safeties, smooth running of the cars under normal and over load conditions, level doors operation, uniformity in rope tension, functioning of individual units like controller, and general performance of the lift installation as a whole shall be conducted.

- The installations shall be got inspected and cleared from the lift inspector, Delhi Govt. by the contractor before handing over the lifts to the department.  The inspection fee shall be borne by the department.

- All instruments and facilities necessary for the tests shall be provided by the contractor.

- After satisfactory final inspection as stated in para 1.10(iii) the contractor shall demonstrate the trouble free running of the lift for a period of a not less then 30 days, before the department takes over.

  - COMPLETENSS OF TENDER:

All fittings, equipments, accessories, hardware, foundation bolts, terminal lugs for electric connections, cable glands and items which are necessary for efficient assembly, shall deemed to have been included in the scope of work.  The installation shall be completed in all details even where such details have not been mentioned in these specifications.

  - COMPLETION DRAWINGS AND DATE:

On completion of work, the contractor shall supply three sets of the followings drawings/data:- for each set of lifts:

- Electrical wiring diagram.

- Detailed schedule of maintenance.

- Lubrication chart operation manual.

- Manufacturer operation manual.

- Spare parts manual.

If the above information and drawings are not furnished, a sum of Rs. 10,000/- for each set of lifts will be deducted from the bills of the contractor.

1.13	MAINTENANCE:

The free comprehensive maintenance including attending to break down, repair/replacement of defective components with new ones etc. for a period of 12 months from the date of handing over of each lift to DDA shall be provided by the contractor.  This service shall include regular examinations of the installations during regular working hours by trained employees of the firm and shall include all necessary adjustments, greasing, oiling, cleaning, supply of genuine spare parts for replacement to keep the equipment in proper condition and the record of the same shall have to be maintained.  The contractor shall provide 24 hours call back service facility.

2.	COMMERCIAL TERMS:

2.1	The rates tendered by the contractor shall be firm and should be inclusive of all central/state Govt. taxes, duties and levies.  No escalation in tendered rates shall be permitted except as in the printed conditions of the contract.

2.2	Concessional Sales Tax form C/D shall not be issued by the department.

2.3	The work shall be considered as one package and indivisible except the comprehensive maintenance work.

2.4	Additional feature other than mentioned in NIT, if offered, shall not be given any weightage.

2.5	TERMS OF PAYMENT:

2.5.1	80% payment on prorate basis shall be released on receipt of equipment in good condition at site along with necessary test certificates.

2.5.2	10% on prorate basis shall be released on satisfactory completion on installation of lift/lifts.

2.5.3	Balance 10% on prorate basis shall be released after handing over of lift/lifts to the department.

2.6	TENDER OPENING:

2.6.1	The tenderer shall submit the bid in two separate sealed envelopes, viz, one containing technical bid and the other containing price bid.  Both the bids should be submitted simultaneously.  The name of the work and also the work “technical bid only” or “Price bid only” as the case may be should be clearly written on top of the respective sealed covers.

2.6.2	The technical bid shall be opened first on the due date and time, as notified, in the presence of tenderer or their authorized representatives who may wish to witness the opening.

2.6.3	Scrutiny of the technical bid shall be done by the department.  Necessary clarification, as may be required, shall be furnished by the tenderers within the time given by the department for the same.

2.6.4	Financial implications, if any, due to any change done in the technical bid during the technical negotiations shall be given by the tenderers in a separate sealed cover, indicating the financial effect to the extent of deviations in their respective technical bid but shall not be allowed to amend/modify the original price bid.

2.6.5	The original price-bid along with financial implication due to technical deviation, if any submitted by the tenderer shall be opened on the date and time (which shall be duly notified to the tenderers) price bids of only those tenderers shall be opened whose technical bids are found acceptable.

3.	WARRANTY:

3.1	All equipments supplied and installed covered by warranty for one year from the date of handing over of each lift against defective design, manufacturer workmanship and installation. If any equipment is found defective due to any of the above cause, the same shall be repaired and/or replaced at site free of charge, by the contractor at his own cost during the warranty period. The warranty shall cover consequential damages to the equipments supplied and installed by him. All repairs/replacements shall be done promptly within a reasonable period.

4. 	GUARANTEE:

The tenderer shall guarantee the entire lift installation as per specifications for a period of 12 months from the date of handing over of the each lift to the department.  The installation shall be covered by the condition that the whole installation or any part there of found defective within the guarantee period shall be replaced by the contractor free of charge in reasonable time to the satisfaction of Engineer-in-charge.  The guarantee shall cover the following:-

a)	Quality, strength and performance of the material and equipments used.

b)	Safe electrical and mechanical strength of all parts of the equipments under all specified conditions/operations satisfactory performance.

c)	Prompt service during guarantee period.

d)	Attending to consequential damage in the equipments and materials installed by the tenderer.

e)	Satisfactory performance during the guarantee period.

f)	Guarantee period of 12 months for each lift shall be counted from date of handing over of same to the department.

5.	PACKING, FORWARDING, TRANSPORT, UNLOADING & STORAGE:

5.1	GENERAL:

After inspection and clearance by department at the manufacturer’s place, wherever applicable, the contractor shall arrange and co-ordinate with all concerned agencies for proper and expeditious packing, forwarding, transporting, unloading from carriers at site, inspection and storage at site and subsequent transfer to plant room/foundation for erection.

  - PROTECTION & PACKING FOR TRANSPORTATION:

a)	Prior to dispatch all plant shall be adequately protected by painting or by other approved means for the whole period of transit storage and erection against corrosion and incidental damage, including the effect of vermin, sunlight, rain, hot and humid climate.

b)	All items of plant shall be clearly marked for identification against the packing list.

c)	Every crate or package shall contain a packing list in water proof envelope.  A duplicate copy of the packing list shall be sent by post to the Engineer-in-charge.

6.	INSURANCE:

6.1	The contractor shall include storage cum erection insurance right from the storage to commissioning of various equipment.  All insurance which the contractor is required to enter into under the contract shall be affected with any authorized general insurance company & terms approved by the Engineer-in-charge and the contractor shall produce the policies of insurance.

6.2	REMEDY OF FAILURE TO INSURE:

If the contractor fail to effect and keep in force the insurance referred to in the proceeding sub-clause the department may effect and keep in force and such insurance and pay such premium as may be necessary for that purpose and from time to time deduct the amount, so paid by the department, from any money due or which may become due to the contractor or recover the same as debit from the contractor’s bill.

6.2.1	The department will not be liable for any damage, losses and compensation payable at law in respect of or in consequence of any accident or injury to any person.

6.2.2	The lowest tender will be decided on the basis of item No. 1 to 4 collectively.  However initial agreement shall be drawn for item No. 1 & 2 only.  For item No. 3 & 4 separate agreement shall be drawn after the completion of main agreement.  The terms and conditions of comprehensive maintenance i.e. for item No. 3 & 4 shall be as under:

TERMS AND CONDITIONS FOR COMPREHENSIVE

MAINTENANCE WORK ITEM No.3 & 4 OF SCHEDULE OF WORK

7.0	A separate agreement shall be drawn for item No.3 & 4 after completion of the item No. 1 & 2.

7.1	The contract for AMC shall be for the period of five years & shall come into force after the expiry of guarantee period of 12 months.  The security deposit i/c performance guarantee @10% for item No.3(e) & 4(e) shall be retained by the department from the security deposit of the main agreement and shall be released after completion of comprehensive maintenance contract.

7.2	The firm shall depute trained technical person directly employed or supervised by them, the technical person shall be qualified to keep the equipment properly adjusted and shall be responsible to maintain the elevator equipments in proper condition, examine, adjust and lubricates the elevator components as required.

7.3	The agency will take all reasonable care and precaution in seeing that the elevators are Safe for use and are in good operating condition.

7.4	The agency during normal working hours shall send at regular intervals and or frequently but at least once in a month, a technician to inspect, adjust and lubricate the parts of the elevator necessary to maintain the elevator in Satisfactory working condition.  The agency will supply all lubricants necessary for the purpose.

7.5	After receiving intimation from the department regarding break down or failure of the elevator, the agency shall send, as soon as possible technician to carry out necessary repair in order to restore the elevator to satisfactory working condition.

7.6	The firm shall submit the preventive maintenance schedule and shall carry out the work accordingly.

7.7	In performing the services as mentioned above, the firm will replace or rectify identical or equivalent item, any component of the elevator rendered defective (with the approval of Engineer-in-charge) due to normal wear and tear and arising out of ordinary and reasonable use of the elevator except for such items as mentioned below:-

i)	Elevator car enclosure (inside).

ii)	Elevator car and landing door panels.

- Bulbs (indicator bulbs, fluorescent tubes) and alarm bell/buzzer.

- Cabin fan.

- Incoming electrical wiring up to main switch in the machine room.

- Main switches in the machine room.

- Intercom and telephone wiring upto machine room.

- The firm will not be liable to replace or repair free of cost under this contract any damage caused to all or part of the elevator as a consequence of fire, water seepages, flooding etc.

- Dry cells and batteries.

- Decorative items including mirror and hand rail.

7.8	The agency has to provide technical assistance on the behalf of the department and suggest improvement as and when required to the department.

7.9	All repair work shall be attended during normal working hours of the normal working days with department representatives not below the rank of Junior Engineer present at the time of repair or the replacement of the required parts.

7.10	The firm shall be clearly exhibit caution board wherever required.

7.11	The agency shall get the license of the lift renewed from the License Authority i.e. Electrical Inspector (lift) during the contract period.  However required fee shall be borne by the department.

7.12	The A.M.C. can be terminated at any time after giving 15 days notice.

TECHNICAL SPECIFICATIONS FOR ITEM NO. 1 & 2

1.0	The lift shall work on micro processor based control system with self diagnostic features, site programming to suit the changing need of the user.  The lift shall be silent in operation & shall have smooth and controlled acceleration and de-acceleration with leveling accuracy of + 5mm.

2.	TECHNICAL PARTICULARS:

2.1	Size of lift shaft	1900mm x 1900mm

i)	Type of lift	Passenger

ii)	No. of lift	Item No.1 – 2 Nos.

Item No.2 – 2 Nos.

iii)	Rated Speed	1.5 metre per second

iv)	Rated load	544 kg. (8 passanger)

v)	Travel	Item No. 1-24 metres appx. (one way)

Item No. 2-30 metres appx. (one way)

vi)	No. & names of floor served	Item No. 1 : 9 Nos. (G+8)

Item No. 2 : 11Nos. (G+10)

vii)	No. of openings	Item No. 1 : 9 Nos.

Item No. 2 : 11 Nos.

viii)	Position of machine room	Above the lift well

ix)	Position of counter weight 	Rear side of lift car

x)	Type of operation	Automatic group supervisory control

With/without attendant.

xi)	Type of control	A.C. drive variable voltage variable	frequency with Microprocessor based 	group control system.

xii)	Type of car doors	Centre opening stainless steel sliding 	door in the moon rock finish.

xiii)	Door operation	Automatic power operated

xiv)	Construction, design &	Stainless steel body with moon rock 	finish on

finishing of car body	3 sides and plain finish on front side shall be 	given. The car shall be complete with PVC 	flooring & toe guard of adequate depth cabin 	fan light fittings with 	lamps and false ceiling. 	Stainless steel hand 	rails shall also be 	provided on 3 sides. Disable friendly lift in 	each lobby shall be suitable for 	handicapped persons. (For this purpose the 	railing and controlling switches etc. shall be 	fixed at 	the appropriate height).

2.2	LANDING DOORS:	Centre opening sliding power operated 	stainless steel doors in moon rock finish & 	shall have a fire resistance of not less than 	one hour

2.3	TYPE OF SIGNAL 	All signal & operating fixtures shall be SYSTEM:	provided with stainless steel face plates.

a)	Call registration indication in buttons of operating panel.

b)	Digital car position indicator in car.

c)	Digital car position indicator with up & down direction on all floors separately for each lift.

d)	Luminous hall call buttons on all floors.

e)	Maintenance free re-chargeable battery operated alarm bell &emergency light.

f)	Fire man’s switch at ground floor for each ground of passenger lift.

g)	Over load warming with visual indication ‘OVER LOADED’ and audio beep of over loading inside the car.

h)	Voice announcement system having standard features.

i)	Intercom system in each lift for communication between the passengers in the elevator & fire control room & machine room (press & speak type) with rechargeable maintenance free battery backup.

2.4	ELECTRIC SUPPLY AVAILABLE:

1)	415 volts, 3 phase, 4 wires, 50Hz A.C. for hoist machine.

2)	220 volts, A.C. 50 Hz.  For car light & fan.

2.5	RESCUE DEVICE:

The elevator should be equipped with manual as well as automatic rescue devices.

a)	Hand Winding Wheel/Handle:

When lift stops due to any reason, it should be possible to move the lift car to the nearest landing manually.  This manual operation should be by means of winding wheel/handle to be mounted on the end of the motor shaft.  The up or down direction of the movement of the car should be clearly indicated on the motor or suitable location for reference during such operation and door should also open so that the passenger may come out of the lift.  The warning plate written in bold signal red colour to switch off the mains supply before releasing the brake and operating the wheel and handle should be permanently displayed.

b)	Automatic Rescue Device:

The lift should be equipped with automatic rescue device, so that in case of lift stops due to any reason, it should automatically reaches to the nearest landing & doors should also open automatically so that the passengers may come out.  The system should have adequate maintenance free rechargeable battery backup.

2.6	Infra red beam type door safety device shall be provided for full height of door.

2.7	Wherever required only copper conductor cables shall be used.

2.8	Microprocessor based control system shall have in built voltage stabilizer to take care of voltage variation to + 10% to – 20% on 415 volt.

2.9	Supplying & installation of landing facia plates made of steel, car apron plate, sill support angle with necessary clamps foundation bolts, support etc. as are necessary in connection with the installation of the lift.

LIST OF ACCEPTABLE MAKES/MANUFACTURERS

S. No.	Make	Manufacturer

1.	OTIS	M/s OTIS Elevator Company (India) Ltd.

2.	KONE	M/s KONE Elevator India Pvt. Ltd.

3.	Mitubushi	M/s ETA MELCO

4.	Schindler	M/s SCHINDLER(I) Ltd.