DELHI DEVELOPMENT AUTHORITY                                    ESTIMATED COST RS: 65721

ELECTRICAL DIVISION NO. 8                                            EARNEST MONEY 1314/-

SCHEDULE OF WORK                                                 DATE OF SALE 22.06.2007

DATE OF OPENING 22.06.2007

Name of Work	:-	M/o Various office building under NZ – (SH : Rewiring of 3 Nos. office barracks and repairing of compound lights at office complex near T.V. Tower. Pitampura)

|  | S. No. |  | Description of Item | Qty. | Unit |  | Rate | Amount |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1. |  | Rewiring for light point/fan point/exhaust fan point/call bell point with 1.5 sq.mm. PVC insulated copper conductor cable in existing surface/recessed steel conduit i/c dismentalling etc. as reqd. (Gr.A). | 82 Pts. | Each |  |  |  |  |
|  | 2. |  | Supply & fixing of 5/6 Amps tumbler/piano type switch on the existing switch box cover i/c connections etc. as reqd. | 98 Nos. | Each |  |  |  |  |
|  | 3. |  | Supply & fixing of 3 pin 6 Amps socket outlet on the existing switch box cover i/c connection etc. as reqd. | 16 Nos. | Each |  |  |  |  |
|  | 4. |  | Supply & fixing of 3 pin 15/16 Amps tumbler/piano type switch on the existing switch box cover i/c connection etc. as reqd. | 15 nos. | Each |  |  |  |  |
| 5. |  | Supply & fixing of 3 pin 15/16 Amps socket outlet on the existing switch box/cover i/c connections, testing etc. as reqd. |  |  | 15 Nos. | Each |  |  |  |
| 6. |  | Supply & fixing of phenolic laminated sheet cover 3 mm thick in the existing metal box i/c cutting etc. as reqd. |  |  | 6000 sq.m | 1000 Sq.cm |  |  |  |
| 7. |  | Supplying & drawing of following size of PVC insulated copper conductor single core cable in the existing surface /recessed PVC/steel conduit i/c connection, testing etc. as reqd. |  |  |  |  |  |  |  |
| a. |  | 2x1.5 sq.mm. |  |  | 123 Mtr | Mtr |  |  |  |
| b. |  | 2x4 sq. mm. |  |  | 185 Mtr | Mtr |  |  |  |
| c. |  | 4 x 4 sq. mm. |  |  | 40 Mtr | Mtr |  |  |  |
| 8. |  | Supplying & fixing of 5 Amps to 32 Amps rating ‘B’ series MCB of the following poles in the existing MCB DB eomplete With connections , testing & commissioning etc. as reqd. |  |  |  |  |  |  |  |
| a. |  | Single pole & neutral MCB (32 Amps) –‘B’ series. |  |  | 3 Nos. | Each |  |  |  |
| b. |  | Single pole MCB 10/16 Amps ‘B’ series. |  |  | 26 Nos. | Each |  |  |  |
| 9. |  | Supplying & drawing of 2.24 mm dia copper conductor wire for loop ear thing in the existing surface/recess steel conduit/PVC capping along with other wires etc. as reqd. |  |  | 800 Mtr | Mtr |  |  |  |
| 10. |  | Supplying & errection of 2x 16 sq . mm PVC insulated PVC sheathed aluminum conductor single core wire of 1.1KV grade along with 6 SWG GI wire i/c hard wood strips 15 mm thick of suitable length & proper binding , testing etc. complete as reqd. |  |  | 360 Mtr | Mtr |  |  |  |
| 11. |  | Supplying & replacement of following way single pole and neutral sheet steel MCB s distribution board 240 V on surface/recess complete with tinned copper bus bar, neutral link, earth bar, din bar, detachable gland plate, interconnections, i/c painting, ear thing etc. complete as reqd. |  |  |  |  |  |  |  |
| a. |  | 8 way |  |  | 1 No. | Each |  |  |  |
| b. |  | 12 way |  |  | 2 Nos. | Each |  |  |  |
| 12. |  | Supplying & fixing of connection box of size (150x100x75) mm. deep made of 1.6 mm thick M.S. sheet having hinged gasketed cover with locking arrangement 4 way connector, 16 amps, kit kat on the existing pole i.e. just below the existing fitting i/c painting, testing etc. complete as reqd. |  |  | 11 Nos. | Each |  |  |  |
| 13. |  | Supplying & fixing of the following item accessories in the existing 70 watt HPSV fitting i/c connections, testing etc. complete as reqd. |  |  |  |  |  |  |  |
| a. |  | 70 watt lamp. |  |  | 11 Nos. | Each |  |  |  |
| b. |  | Ballast suitable for 70 watt HPSV fittings. |  |  | 9 Nos. | Each |  |  |  |
| c. |  | Ignitor suitable for 70watt HPSV fittings. |  |  | 8 Nos. | Each |  |  |  |
| d. |  | Capacitor suitable for HPSV fittings. |  |  | 8 Nos. | Each |  |  |  |
| 14. |  | Rebate against dismentalled material of existing wiring such as :- |  |  |  |  |  |  |  |
| a. |  | 2x4/2 x 1.5 sq mm PVC insulated Al. cond . and 2.24 mm. dia bare al. cond . wire. |  |  |  |  |  |  |  |
| b. |  | 5/16 amps switch & sockets. |  |  | For 3Nos. Barracks |  |  |  |  |
| c. |  | Old SDB’s (-) |  |  |  | Each |  |  |  |

Executive Engineer(E)

Elect. Divn. No. 8/DDA

ADDITIONAL TERMS CONDITIONS

- The contractor must get acquainted with the proposed site for the work and study specifications and conditions carefully before tendering. The work shall be executed as per programme approved by the Engineer – in –cahrge.

- After the award of the work contractor shall produce samples of all the material to be used in the work for approval of the Engineer-in-charge. Only material confirming to the approved sample shall be used in the work.

- The work as indicated in the schedule Of quantities attached herewith including any modifications, additions/ alterations order subsequently shall be carried out as per CPWD specifications for indicated below:-

  - CPWD specifications for electrical works at Delhi Part-I (Internal) 2005 and part-II (External) 1994 with amendments made upto the date of tender.

  - Indian electricity rules 1956 as amended upto date.

  - A table indicating the makes, governining specifications and other details in respect of some of the important material to be used in the work is attached. These specifications shall have precedence over those indicated in 4.1 above.

  - (a)	  Only material bearing ISI/BIS certifications mark shall be used in the work. Where articles of different designs/ make bearing ISI/BIS certification mark are available, the decision  of the Engineer-in-charge about the design/ make to be used in the work shall be final/ binding on the contractor.

  - (b)  In case material bearing ISI / BIS certification mark are not available, the material shall confirm to relevant BIS specification.

- The earth continuity with wire of 2.24mm dia (4MM) bare conductor shall be taken to terminate in all light points/ fan point/ exhaust fan points/ call bell points.

- Porcelain connectors shall be provided for terminating light points, fan points and call bell points etc. where no fitting is to be provided.

- For light points, fan points, call bell points, light plug points & power plug points, Piano type switches/ sockets outlets/ bell push (as the case may be) shall be provided.

- Three pin type ceiling rose shall be provided for exhaust fan points.

- The screw for fixing phenolic laminated sheet to cover metal boxes shall be of adequate length. The cadmium plated and round- headed screws with fan/ cup washers shall be used.

- All G.I/ MS boxes except telephone boxes shall be earthed.

- Copper bare earth wire in the switch boxes shall be sleeved with close fitted PVC sleeve. The sleeve portion shall be from the end terminal to atleast 5cm inside the conduit.

- The contractor shall be responsible for the watch & ward of electrical installation and all fittings until the work is fully completed and handed over to the department. No claim on this account will be entertained.

- No. T&P shall be issued to the contractor.

- The rates quoted shall be inclusive of all taxes, Govt. duties, cartage and levies if any, nothing shall be paid extra on this account.

- Adequate length of phase and neutral wires of circuit/ submain wiring at both ends shall be extended in order to have proper future maintenance and also proper connection in distribution boards/ main switch-board. The measurement of the circuit/sub-main shall be done upto the termination of the conduit.

- When work is executed in  occupied building there should be minimum of inconvenience to the occupants. The work shall be programmed in consulation with allottees. If as required the work may have to be done even before and after office hours.

- Dismentalling of circuit wire, sub-main wire, etc. from existing conduit shall be made by the contractor within the quoted rates.

- Light fittings shall be dismentalled wherever required for wiring and are to be reinstalled by the contractor within the quoted rates.

- Missing screws for fixing of sheet if required shall be fixed by the agency with in quoted rates.

- Nothing extra on account of cartage shall be paid to the contractor by the department.

- Piano type switch/ socket shall any one of following make

a) Anchor 	b)	CPL	c)	Precision 	d)	cona.

21.     Phenolic laminated sheet shall be any one following make.

a) Hylam 	 b)	formica  c)    Caprihans   d) super hylam.

22.     .PVC insulated copper/ Aluminum wire shall be any one of

Following make.

a) Skytone   b) National   c)    ECKO      e)   Havell’s

23.	   M.V. lamp shall be any one of following make

a)     Philips    b)        Havell’s       c)   OSRAM

Executive Engineer(E)

Elect. Divn. No. 8/DDA