OFFICE OF THE EX.ENGINEER

PRESS NOTICE No.7/EE/ED7/DDA/0708

N.I.T. No.-10

DELHI DEVELOPMENT AUTHORITY

ELECTRICAL DIVISION No. 7

NAME OF WORK	:- D/O land for J.J scheme at sector G -8 sub – city.

SH			:-  supply and installation of sielent D.G set at sector G-8 pocket II 				Narela

| S.No. | Description of item | Qty. | Unit | Rate | Amount |
| --- | --- | --- | --- | --- | --- |
| 1. | Supply and installation testing commissioning of diesel engine driven silent generating set of 40 KVA capacity with 0.8 P.F ( lagging ) capability to develop 415/440V 3 Ph, 50HZ supply directly coupled with water cooled diesel engine of suitable BHP.at 1500 r.m.p batter starting 4 stoke multi cylinder through suitable coupling and coupling guard mounted on suitable size of C.C foundation 1:3:6 and manual control panel with accessories suitable for above said capacity of D.G. set residential silencer with acoustic enclosure necessary accessories and proctection as per terms conditions attached i/c alignement connection inter connections painting earthing etc compete aas required. | 1set | Set |  |  |
| 2. | Earthing with G.I earth pipe 4.5 mtr. long x 40mm. dia i/c accessories and providing masonary enclosure with cover plate having locking arrangement watering pipe etc (;but without) charcoal or coke and salt complete as reqd. | 2set | Set |  |  |
| 3. | Extra for using salt and charcoal for pipe earth electrode as reqd. | 2set | Set |  |  |
| 4. | Earthing with copper plate 600mm x 600mm x 3mm. thick i/c accessories and profiding masonary enclosure with cover plate having locking arrangement and watering pipe etc. (but with out charcoal or coke and slat) complete as reqd. | 2set | Set |  |  |
| 5. | Extra for using charcoal and salt for G.I. or copper plate earth electrode as reqd. | 2set | Set |  |  |
| 6. | Providing and fixing of 25mm x 5m copper strip or surface or in recess for connection etc as reqd. | 30mtr. | Mtr. |  |  |
| 7. | Supplying of 3.5 x 50mm Al conductor PVC sheathed XLPEarmoured cable of 1.1 KV grade i/c testing etc. as reqd. | 30 mtr. | Mtr. |  |  |
| 8. | Supplying and fixing of one number pvc insulated PVC sheathed XLPE aluminium conductor cable of 1.1 Kv grade of size exceeding25 sq.mm but not exceeding 120 sq.mm on surface/cable duct etc as reqd. | 30 mtr. | Mtr. |  |  |
| 9. | Wiring for light point fan point exhaust fan point and call bell point with 1.5 sq.mm PVC insulated copper cond.single core cable in surface /recessed steel conduit with modular swithch modular plate suitable for G.I box and eathing the point with 4mm PVC insulated FRLS copper cond single core cable as earth wire etc as reqd. | 14 Pt | Pts |  |  |
| 10. | Wiring for circuit wiring with the following size of FRLS , PVC insulated copper cond single core cable in surface recessed steel conduit etc. as reqd. A0 2 x 1.5 mm2 x 4 mm2 for eath wire. | 5mtr. | Mtr. |  |  |
| 11. | Supplying and fixing of suitable size G.I box with modular plate and cover in front on surface /recess i/c P/F 15A /16A 6 pin modular socket outet and 15A/16Amp modular switch connection painting etc. as reqd. | 1No. | Each |  |  |
| 12. | Wiring for light point /power pint with 2 x 4 mm2 PVC insulated cond single core cable in surface recessed steel conduit along with 4sqm. PVC insulated FRLS copper cond.cable as earth wire as reqd. | 5 mtr. | Mtr. |  |  |
| 13. | Supplying and fixing 5A to 32A rating 240 v, ( B-series) MCB of following poles in the existing MCB DB complete with connection testing and commissioning etc. as reqd. a) SP, MCB(cat-B) b) SPN,MCB(cat –B) | 4 Nos. 1No. | Each Each |  |  |
| 14. | Supplying and fixing of following way single pole and neutral sheet steel MCB –DB 240 V. on surface /recess complete with tinned copper Bus –bar neutral link earth bar din –bar detachable gland plate inter connections i/c painting earthing etc. as reqd. a) 8 way | 1 No. | Each |  |  |
| 15. | Supplying and fixing of ceiling fan of size 1200mm sweep complete with all accessories i/c connection testing wiring the down rod etc. complete as reqd. | 2 Nos. | Each |  |  |
| 16. | prewised flourecent tube fitting of box type complete with all accessories and 1 x 40 w fluorescent tube direct on ceiling /well i/c connection with 1.5 mm2PVC insulated copper cond.single core cable i/c testing commissioning etc. as reqd. | 6 Nos. | Each |  |  |
| 17. | Providing and fixing of exhaust fan of size 450 mm. sweep along with louvers /shutters complete with frame making the suitable opening and making good the same i/c connection testing etc. as reqd. | 1No. | Each |  |  |
| 18. | Supplying and fixing of street light luminaire of model no.SSO/120/H/W/of crompton Greaves or similar superior make along with suitable ballast with 1 No. 70 watt. SON T. lamp and P/F on existing surface of wall i/c connection testing etc. as reqd. | 2 Nos. | Each |  |  |
| 19. | Supplying and fixing of bracket made out of 40mm. dia G.I pipe (B-class ) 1 Mtr. Long (appx.) dully bend to the reqd.shape for fixing of street light fitting on the wll with M.S clamp nut bolts i/c wiring with 2 x 1.5 mm2 copper conductor PVc insulated cable and testing etc.as reqd. | 2Nos. | Each |  |  |
| 20. | Supplying and fixing of 4 pole 100Amp capacity change over switch OFF –LOAD type with sheet steel enclosure and side handle operated, suitable for operation or 415/volts A.C supply 50HZ i/c connections and testing etc. as reqd. | 1 No. | each |  |  |
| 21. | Supplying and fixing of walll /floor mounted metal boared of walded contructions fabricated with minimum 50mm x 50mm. x 6mm. angle –iron frame work with horixental and vertical inter mediate member of suitable angle /flat iron for mounting of switch geer i/c painting etc. as reqd. | 1.5sqmtr. | Mtr. |  |  |
| 22. | Supplying and fixing chequred /corrugated red /black rubber mat sheet (ISI marked ) suitable for 1.1 KV grade protection of size 2 meter x 1 meter x 10mm thick etc | 1No. | Each |  |  |

ADDITIONAL CONDITNS AND TECHINCAL SPECIFICTIONS

- The contractor must get acquainted with the proposed site for the work and study specifications and condition carefully before tendering. The work shall be per the direction of the Engineer in charge

- The work as indicated in the scope of work attached here with i/c any modification /addition /alteration ordered supsequently ,shall be carried out as per the specifications  given below;-

- CPWD specification for electrical works (part I) Internal 1994 (PartII) external 1995 with correction slips up to the date of the tender

- Relevant I.S modified upto date wherever /I.S code do not exists the British standards shall be followed.

- Indian electricity Rule 1956 as amended.

- A table indicating the governing specifications makes acceptable in respect of some of important material is attached. The contractor, will have option to use any of makes specified in the table against a particular items subject to conformity with specification.

- All the material shall be got approved from the Engineer in charge before installation at site.

- Allminor building work such as cutting of holes and cheses in wals /celling and making good the same with cement mortar of 1:4 ( 1 cement :4 coarse sand)

- Provision of supports and clamps for fixing arrangement i/c nuts bolts cable glands lugs terminals block etc.

- The entire system shall be tested to the satifaction of Engineer in charge.

DISEL CENERATING  SET

- These specifications covers:-

- The details of equipment to be supplied.

- Inspection of equipments as may be necessary before dispatch and celivery.

- Installation testing and commissioning and handing over the equipment in working order to the  deptt.

- The capacity of the generating set shall be 40 KVA for generating 415/440 volts at 0.8.P.F. (lagging) suitable for 50 Hz . 3 Phase 4 wire system Eninge shall confirme to B.S. 5514/BS 649 with 10% over loading for one hour in any 12 houras duration and shall include the following monterings /accessories as per Manufacturers design.

- Exhaust manifola

- Residentaial silencer with suitable pipe length and asbestos rope through out the length of pipe

- Fule pump

- Fule enjectors.

- Fule filtear

- Fule hoses.

- Lub oil pump

- Lub oil filter

- Air intake manifold.

- Air clear.

- Speed governor.

- Electric starter 12 volts D.C

- Fluwheel

- starting switch with key.

- Lub oil pressure gauge.

- Engine operation and maintenance manual

- Part catalogue.

- Emgine maintenance schedule.

- Warranty card.

- Engine routine test certificate.

- Breather -1 No.

ALTERNATOR

Synchronous alternator 40 KVA suitable for continuous operation at 1500 RPM generating 415/440 volts at 0.8 power factor ( lag.) suitable for 50Hz  3phase ( 4 wire) system. The alternator shall be self excited self regulated, foot mounted fitted with by and / or roller bearing. The alternator will be suitable for tropical climate and shall generally confirm to IS : 4722/BS-2613

- MANUAL CONTROL PANELThe control panel body will be fabricated out of 14.S.W.G. thick M.S. sheet the panel board will be suitable for floor mounting indoor installation dust and vermin proof. Copper conductor PVC insulated control cable of size 2.5 sq.mm. shall be used. Cable shall be ferruled for proper maintenance /checking wiring of panel; shall be equipped with the following :-

(i)  MCB of suitable size 	1No.

(ii) Ammeter with selector switch  1No.

(iii)voltmeter with selector switch 1No.

- Instrument fuses	 1set.

- Pilot lamp for running on load .1 set.

- Incoming and out going termination 1 set each

- FUEL TANK

(a) Adoptor for supply hose pipe		1No.

(b) Adoptor for return hous pipe 		1No.

(c) drain cock				1No.

(d) Breather 				1No.

(e) Level indicator tube with scale 	1No.

- The coshall be supply the following cools with the D.G. sets free of cost as follows.

(a) Double end spanner (Gasore/Taperia)make		1 set or 12 Nos.

(b) Ring spanner 		do				4Nos.

(c) screw Driver		do				2 No. (10”&8”)

(d) screw Driver		do				1No.

(e)  Adjustable  wrench Hammr				2 No.

(f)  Goti set oil pump 	( Gadore /Taparia) make	1 set

- SOUND ATTENUATED SYSTEM : (SOUND FROOF ENCLOSURE)CONSTRCTION

- The enclosure shall be designed for easy access to serviceable parts,and easy assembling and dismentalling etc.

- All the section holding generator base i.e base frame shall be fabricated with (150 x 75) mm. channel(ISMC).

- All the body of enclosure shall be fabricated of 14 SEG CRCA sheet metal components seven tank pretreated and pinted with polyster based powder coated ( inside as well as outside)

- Nut – builts hadware shall be zinc coated

- In built fuel tank shall be paced with breather drains plug for filling and draining diesel.

- The door should be enclosure

- The batteries shall be palced separately inside the enclosure.

- The door should be gasketted with high quality EPDM gaskets to avoid leakage of sound.

- The sound proofing of enclosure should be done with high quality rock wool /mineral wool confirming to IS :8183 .The rock wool should be further covered with fibre glass cloth and perofrated powder coated CRCA sheet.

- Specially designed sound attenduators shall be provided to control sound at entery and exist points inside the enclosure.

- Asequate ventilation should be provided to meet air requirement for comnustion and heat removal by providing a blower to meet totally air requirement and air change so that the temperatutes of enclosure canopy does not exceed 5 degree centigrade of ambient temperature.

- The arrangement for illumination inside th enclosure. Shall be done to the satisfaction of Engineer in charge

- The door handles shall be lockable type.

- The design of capony should be suggested or approved by engine manufacturer, and cerfificate to this effect that the engine /warrancy /gurrantee from engine /generator manufacturer stands for the complete diesel engine generating set in the  acostic enclosure.

- The noise level should be 75 d BA (MAX) at a distance of 1 mtr.

- Limergency stop push bution outside the enclosure.

- Separate doors of engine and alternative shall provided

- All the material used for conopy air duct should be weather proof.

- The contractor shall furnish the manufacturer test certificate at the time of supply.

- THE FOLLOWING ARE ACCEPTABLE MAKES:-

| 1. | Change over switch | Standred, Havells L& T make. |
| --- | --- | --- |
| 2. | Acoustic enclosure | power shall make, Jakson make and MIRACO Sudhear Engg.& poweica ltd. |
| 3. | Alternator | Kirlosker Elect .co. ltd. Jyoti Ltd. Stam ford. Crompton. |
| 4. | Diesel Engine | Cummins /Ashok Trayland kirlosker oil Engines Ltd. |
| 5. | Cables | Skytone /Ecko/ Nicco /Asian /Unistar |
| 6. | Battery | Exide /standred / Furukwa /Chloride India Ltd. /AMCO |
| 7. | Instruments and meters. | AE/LT&LK/ Goyala |
| 8. | Modular switch /socket out set | Anchor (Roma) clipsal (opale) /MDS (legrand) |
| 9. | Steel conduit | BEC/AKG/VIKAS/Steel kraft /NIC |
| 10. | PVC insulated copper wire | Sky tone /National /ECKO/HAVELLS |
| 11. | MCB | Standard /L&T /MDS/ Indokopp/Action |
| 12. | Street light luminaire | Box type tube fitting /lamp |
| 13. | Ceiling fan and Exchaust fan | Crompton, Bajaj, Khatan |
| 14. | Rubber mat | ISI – Marked |

- The contractor shall submit completion certificate as per appendix ‘F’ of the general specifications for electrical work (part –I) Internal 1994 one month after actual date of completion failing which an amount of Rs. 5,000/- (Rs. Five thousand only) shall be dected from any amount due to the contractor from DDA

- Drawing showing the layout of internal electric installation are attached herewith. The Engineer in charge reserves right to make any modifications in the layout at any stage during the execution of work. No extra under the provisions of clause 12 and 12-A in the printed conditions of the contract.

- After the award of work the contractor shall produce samples of all the materials to be used in the work for approval of the Engineer in charge..

Only materials conrforming to the approved sam ple shall be used in thework. The sample shall be preserved till the completion of the work. If required the sample installation shall also be executed by the contractor in selected sample units at appropriate time as per instruction of the Engineer in charge. The decision of the Engineer in charge regarding make of the materials shall be final /binding on the contraector.

- In case of any discrepancy in the description of any item given in the schedule of quantities and the specifications the former shall prevail. If the specification of any item are not available, the decision of the Engineer in charge shall be final.

The specifications given in the following clauses shall have precedence over those indicated in para above in case of deviation between  the two.

- Chases /recess cut in the masonary for embedding the conduit, boxes and DBS etc. shall be in proper line and to the required depth. Any consequential damages shall be made good to the satisfaction of the Engineer in charge. After the coduit/ boxes etc. are fixed the chases /resess shall be filled with cement motar 1:4 (1 cement ,4 coarse sand) and made flush with the masonary surface and cured adequately.

- orizonal chase more than 60 cm shall not be allowed.

- The recessed M.S condit in wall shall be fixed by means of iron hooks at suitable as  per specification. These shall be fixed so as the M.S conduit is not damaged.

- The contractor shall ensure that conduit laid id free from any concrete slurray/ building material etc. For this purpose thorough checking GI fish wire of at least . 1.2 mm dia shall be drawn which shall be remoced at time of wiring.

- The galvanized metal boxes to be used in the work shall be made of M.S sheet .Any of the following sizes suitable for iccimmidating the accessories like switches , sockets fan ragulator etc. shall be used. The minium dupth of metal boxes meant  for accommodating fan regulator shall be75mm

  - 75mm x 75mm x 60mm deep

  - 100mm x 100mm x 60mm deep

  - 180mm. x 100mm x 60mm deep

  - 200mm x 250mm. x 75mm deep

  - 100mm x 75mm x 60mm deep

- After plastering by civil agency the edges for switch  boxes fan boxes and junction boxes etc. shall be neatly finished by electrical contractor with 1:4 cement , fine sand mortar.

- Any ordinary or special accessories i.e. PVC  or metal boxes id required for the purpose of branching of conduits shall form part of the submain /circuit /point wiring. Further conduit work includes fittings such as a junction boxes , bends, couplers etc.

- The earth continuity with wire of 2.24 mm dia (4mm2 ) copper conductor shall be taken to terminate in all light points /twin control light points /fan exhaust fan points /call bell points.

- No looping through horizontal conduits in the wall shall be permitted except  wherever specifically desired or approved by Engineer in charge

- The light points where no fitting is to be provided under this contract shall be provided with extended wire for phase & neutral for at least 25 cm in length.

- for celain connectors shall be provided for rerminating light point cell bell points etc. where no fitting is to be provided.

- For light points fan points call bell points light plug points & power plug points modular type switches /sockets out lets/ bell push (as the case may be ) shall be provided.

- Socket out let for power plug points shall be six –pin type.

- Three pin type ceiling rose shall be provided for exhaust fan points.

- The screws for fixing phenolic laminated sheet to cover metal boxes shall be of adequate length. The cadmium plated and round headed screws with flat /cup washers shall be used

- Adequate length of phase and neutral wires of circuit /submain wiring at both ends shall be extended in order to have proper future maintenance and also proper connection in distribution board /,\main shall be done upto the termination of the conduit

- All G.I. /M.S. boxes shall be earthed

- The work shall be carried out in processed M.S conduit wiring system.

- The payment for conduit work shall be made after the fish wire is drawn.

- Embeding of earth electrode and its testing shall be carried out in the presence of Engineer in charge or his representative

- The contractor shall be responsible for the watch and ward of entire electrical installation and handed over to the department. No. claim on this account will be entertained.

- Guarantee period of 12 month shall be counted from the date of handing over of installation to the department against manufacturing defects /satisfactory performance on non judicial stamp paper of Rs. 50/- only.

TABLE INDICATING GOVERNING SPECIFICATION ETC.IN RESAPECT OF MATERIAL TO BE USED AT WORK

| S.No. | ITEM | GOVENRING SPECIFICATIONS | REMARKS |
| --- | --- | --- | --- |
| 1.(a) | Steel Conduit | IS:9537 part II 1981 | For temination of steel conduit in boxes check nut and bushes are to be used. |
| 2.. | PVC insulated copper conductor wires | IS:694-1990 | - wires of size 2.5 mm2and above shall be stranded type - end termination of all stranded wires shall be done by means of crimped copper lugs. - All cable lugs should bePVC taped /sleeved at end terminals |
| 3. | M.C.Bs | IS:8828-1996 | Minimum breaking capacity 10KA at 240/415 volts. |
| 4. | Phenolic Laminated sheet | IS:2036-1974 | The sheet shall be 3mm thick the sheet shall be cut vertical & edges rounded off. |
| 5. | Brass Batten Holder | IS: 1258-1987 |  |
| 6. | (B) C.I.Junction | IS:2667 | Junction boxes for use in ceiling shall be miniumun 60 mm deep and on wall minimum 35 mmdeep |
| 7. | M.S.Bend Coupler &Elbow | IS: 2667 |  |
| 8. | Modular /Piano Switches 6A/16A | IS:3854-1997 | Shall be white in colour |
| 9. | Modular /Piano three /Six Pin Scoket outlets 6A/16A | IS: 1293-1989 | Shall be white in colour |
| 10. | G.I.Boxes | Galvanized class –P-1 as per IS : 277-1977 | - shall be made out of 18 SWG M.S sheet up to size of 200mm x 30mm & above this size boxes shall be made out of 16SWG M.S sheet. - The earth terminal of suitable size of bolt duly welded nut and spring washers shall be provided for the terminaton of earth wires. |