OFFICE OF EX.ENGINEER

ELECTRICAL DIVISION 7

PRESS NOTICE NO. 6/EE/ED-7/DDA/07-08

N.I.T NO.- 11

SCHEDULE OF WORK

NAME OF WORK	:- M/o various scheme (296,38) acre under North Zone N.A. I

SUB HEAD		:-  Supply & installation of submersible pump set at Northern Ridge.

| S.No. | Description of items | Qty. | Rate | Unit | Amount |
| --- | --- | --- | --- | --- | --- |
| 1. | Supplying of submersible pump set duly coupled with suitable rating of 3 phase 415 volts, 50 Hz 2900RPM submersible induction motor the pump set shall be suitable for the follows duties: A. a)Discharge 170LPM 2Nos. b) Head 35 mtr. c) clear water Liquid :clear water B. a) Discharge 170LPM b) Head 14mtr. 1 No. c) Liquid clear water | 3set | Set |  |  |
| 2. | Supplying of following size GI B-Class pipe i/c GI flanges duly screwed and welded on both ends of GI pipe bend tee, nipple rubber gasket GI nuts, bolts ,and washers etc. as reqd. a)50mm dia b) | 45 mtr. | Mtr. |  |  |
| 3. | Supply of PVC sheathed PVC insulated copper conductor submersible cable as reqd. a) 3 x 1.5 sq.mm. | 70mtr. | Mtr. |  |  |
| 4. | Lowering testing commissioning of submersible pump set along with double flanged GI pipe submersible cable i/c jointing and accessories upto the required depth providing and finding 2 Nos. Ms. clamps made of MS flat 75 mm x 10mm. x 500mm. along with nuts bolts washers cutting the existing bore cover making suitable removable cover and fixing of submersible cable with insulated wire with GI pipe complete as reqd. | 2No. | Each |  |  |
| 5. | Supply & fixing of following size of GI flanged calves complete with rubber gasket nuts bolts and washers et. As reqd. a) Non – return valve ( without by pass) | 2No. | Each |  |  |
| 6. | Supply erection testing and commissioning of Lt feeder pillar fabricated out of 14 SWG (2mm thick nominal) CRCA MS sheet with 40mm x 40mm x 6 mm angle iron legs as per drawing –g attached and suitable to accommodate and supplying and fixing the following accessories there in i/c connections iter connections with suitable size of copper wire earth connections numbering and spray painted after applying a coat of zinc chromate primer as reqd. - 32 amp. TP&N MCB 10KA ( C- Series) - 20 amp . TP&N MCB 10KA (C-Series ) - DOL starter with enclosure having suitable relay complete as reqd. - Single phase preventor –cum –water level guard with prod / sensor - 3 phase shunt capacitor suitable for item no - phase indicator neoin lamps with toggle switch and back up fuse - voltmeter (0 to 500volts) 96 mm. squire dial with selector switch - ammeter (0 to 300amp) 96mm. sq mm. Dial - 20 amp. TP MCB 10KA (B- Series) - 6 amp. TP MCB KA ( B-Series) - 4 strip 300 mm. long al bus bar 100amp. Capacity duly PVC tapped sleeved having drilled holes, 6 mm. dia bolts nuts washers etc. as reqd. - Danger Notice plate - 20 amp industrial socket | 1No. 1Nos. 1No. 1No. 1No. 1No. 1No. 1No. 1set 1No. 1No. | Each Each Each Each Each Each Each Each Set Each Each |  |  |
| 8. | Supply & fixing 25 mm x 5 mm GI strip at 0.5 m below ground level as strip earth celectrode i/c soldering etc as reqd. | 65 mtr. | Mtr. |  |  |
| 9. | Providing and fixing 25 mm x 5 mm GI strip on surface or in rece ss connections etc as reqd. | 15mtr. | Mtr. |  |  |
| 10. | Providing and fixing 6 SWG wire from pole to pole as reqd. along with existing w-ires/ cable etc. as reqd. | 925 mtr. | Mtr. |  |  |
| 11. | Laying of 1 No. XLPE al cond. Armoured cable of 1.1 KV grade not exceeding 25 sqm. From pole to pole with the binding wires etc. as reqd. | 925 mtr. | Mtr. |  |  |

MAKES OF MATERIAL AND GOVERNING SPECIFICATIONS

| S.No. | ITEM | GOVERNING SPECIFICATION | MAKES |
| --- | --- | --- | --- |
| 1. | Submersible pump set | -- | K.S.B. /Kiroskar/Crompton/Greaves |
| 2. | C.I. Sluice Valve | IS: 14846 | I.V.C. /Kiroskar |
| 3. | C.I Non return valves | IS: 5312 | I.V.C /Kiroskar |
| 4. | G.I pipe | IS: 1239 | Jindal (Hissar ) /Surya /TATA |
| 5. | Starter | -- | L &T /Siemens/Cuttler Hammer |
| 6. | Shunt Capacitor. | -- | GE/Madhav/Crompton/L&T |
| 7. | Single phase preventor –cum water level guard | - | L & T Minilec |
| 8. | Ammeter & voltmeter | IS: 1248 | AE/Havells/UEL/IMP |
| 9. | PVC sheathed PVC flat submersible copper cable | IS: 694 | Plaza /Finolex/ Safex. |
| 10. | Selector switch | -- | Hsvells/Thakur/ L & T /KAYCEE |
| 11. | PVC Insulated copper wire | IS:694 | Sky tone /National /ECKO/Havells. |
| 12. | M.C.B. | IS. 8828 | Standard/L&T/MDS/Indokopp/Action |
| 13. | PVC sheathed PVC XLPE AL armoured cable | 7098 | Asian cable/ Unistar/Ecko/ Nicco Skytone |
| 14. | Panel Board | -- | Shall be fabricated as per drawing attached |

ADDITIONAL CONDITIONS AND SPECIFICATIONS

- The contractor must get acquainted with the proposed site for the work and study specifications and conditions carefully before tendering. The work shall be executed as per programme approved by the Engineer in charge. The work shall be executed in close coordination with the progress of the bldg. work. If the site for electrical work is not available in part or in full for any reason whatsoever the time for the execution of the electrical work shall be correspondingly extended. No claim for any idle labour or compensation (except as provided under clause 10C/10CC as applicable in the printed conditions of contract shall be enterntained.

- The contractor shall submit completion certificate as per appendix ‘E’ of the general specification for electrical work ( part –I I) internal -2005 within one month after actual date of complete failing which an amount @ 1% of the tendered cost subject  to maximum of Rs.5,000/= shall be deducted from any amount due to the contractor from DDA.

- No. tubewell bore shall be left open as & when sub P/Set are taken out for repair / replacement.

- The following work shall be deeme to be included within the scope of work to be executed by the contractor and nothing extra shall be paid on this account.

- All minor building work such as cutting of holes and chases in walls ./ ceiling and making good the same with cement mortar 1:4 (1 cement and 4 coarse sand)

- Provision of suitable support and clamps for fixing arrangement including nuts, bolts, cable glands, lugs terminal blocks etc. as a part of the particular item unless given separately in the schedule of work.

- Masonry support / G.I pipe support etc. shall be provided wherever required.

- Testing of installation :

- The entire system shall be tested to the satisfaction of Engineer in charge

- Tests shall be performed in the presence of Engineer in charge or his representative.

- The contractor shall provided all labour , equipments and material required for performance of the tests.

- The rates quoted by the contractor shall be firm and should be inclusive of all Central/ State Govt. Taxes Duties and Levies etc

- Concessional sales Tax From C/D shall not be issued by the Department.

- The installation shall be covered by the conditions that the whole installation or any part there of found defective within the guarantee period should be replaced by the contractor free of charge in a reasonable time. The guarantee shall  cover the followings :-

- Quality strength and performance of the material and equipment used.

- Safe electrical and mechanical strength of all parts of the equipment under all specified conditions of operations / satisfactory /performance.

- Safe performance figure and other values as specified in the schedule of guarantee /technical particulars.

- Prompt service during guarantee period

- Attending to consequential damages in the equipments supplied and installed by the tenderer.

- Guarantee period of 12 month shall be counted from the date of handing over of installation to the department against manufacturing defects /satisfactory percformance on a non judicial stamp paper of Rs. 50/ only.

- Contractor shall provided the manufacturer tes certificate in respect of all major items.

- The contractors shall be fully responsible for watch and ward of the material brought /work executed at site till the same is complete and taken over by the department.

- After the ward of work the contractor shall get all the materials approved from the Engineer in charge before use in the work. The contractor shall also produce test certificate for conformity with relevant IS specification if required by the Engineer in charge.

- The submersible cable from panel T.W bore shall be laid in 40mm dia G.I.B. class pipe the cost of which is included in the item of panel board.

- flyash bricks shall be used in the work wherever required

- SPECIFICATIONS

The work as indicated in the schedule of quantities attached herewith including any modifications additions alterations ordered subsequently shall be carried out as per specifications given below:

  - CPWD specifications for electrical works at Delhi Part –I (internal) 2005 and  part II (External) 1994with amendments up to the date of tenders.

  - Indian Electricity Rules 1956 as amended up to date.

  - A table indicating the makes governing specifications and other details in respect of some of the important materials to be used in the work is attached . These specification shall have preference over those indicated in 14 (i) above.

  - Only material bearing ISI/BIS certifications mark shall be used in the work. Where articles of different designs / make bearing ISI/BIS certification mark are available the decision of  Engineer in charge about the design / make to be used in the work shall be final and binding on the contractor .

  - Where material bearing ISI/BIS certification marks are not available material conforming to relevant BIS/ISI shall be used with prior approval of Engineer in charge.

  - If the specifications of any item  are not available then the decision of the Engineer in charge regarding quality shall be final and binding on the contractor.

- In case of any discrepancy in the description of any item given in the schedule of 	quantities and the specifications the former shall prevail if the specifications of any 	item are not available the decision of Engineer in charge shall be final.

- No tool and plants shall be issued for execution of the work or for testing of the 	installation . These shall be arranged by the contractor with in the quoted rates.

- The contract would have to make his own arrangement for cartage and transportation 	of the materials and nothing extra shall be payble on this account.

- sub. Standard work shall be rejected without assigning any reason.

- The following information to be  furnished by the tenderers

    - Type make model and HP of the pump set offered.

    - Discharge in liters per minutes and head in meters.

    - Revolution per minutes.

- Time allowed for carrying of work within one months

- Additional specifications are indicated in the following clause. These additional 	specifications given below shall have precedence over these indicated pare 14 above 	in case of deviations between the two.

- Three pin socket outlet shall be provided for power plug points.

- Connectors to be used any where in the installation shall be of porcelain type.

- Earthing work i.e. embedding of earth electrical and testing of installations shall be 	carried out in the presence of the Asstt. Engineer (E)

- The length of GI pipe to be used in the work for installation of the submersible pump 	set shall not be more than three meters.