DELHI DEVELOPMENT AUTHORITY

ELECTRICAL DIVISION NO. – IV

## SCHEDULE OF WORK

Name of Work 	:  -	M/o Completed scheme of  Nazul A/c – II under S.W.Z.

SH. 	 : - 	Supply and Installation of additional submersible Pump Set at ‘B’ Block Distt. Park, Janak Puri.

| S.No. |  | Description of items | Qty. | Rate | Unit | ### Amount |
| --- | --- | --- | --- | --- | --- | --- |
| 1. |  | Supply of Submersible pumps duly coupled with suitable rating of 3 phase 415 volts, 50 Hz, 2900 RPM, (nominal) submersible induction motor. The pumpsets shall be suitable for the following duties :- |  |  |  |  |
|  |  | - Discharge : -160 LPM - Head :- 45 mtrs. - liquid :- Clear water | 2 sets |  | Set |  |
| 2. |  | Supplying of following size of G.I. B Class pipe including GI flanges duly screwed and welded on both ends of G.I. pipe, bend tee, nipple, rubber gasket, G.I. nuts, bolts and washers etc. as reqd. - 50mm dia | 84 mtr. |  | Mtr. |  |
| 3. |  | Supply of PVC sheathed PVC insulated copper conductor submersible cable as reqd. - 3 x 1.5 sq.mm. | 100 mtr. |  | Mtr. |  |
| 4. |  | Lowering, testing, commissioning of submersible pumpset along with double flanged G.I. pipe submersible cable including jointing and accessories upto the required depth, providing and fixing 2 Nos. M.S. clamps made of MS flat 75mm x 10mm x 500mm along with nuts, bolts, washers, cutting the existing bore cover, making suitable removable cover and fixing of submersible cable with insulated wire with G.I. pipe complete as reqd. | 2 Jobs |  | P/Job |  |
| 5. |  | Supplying erection, testing and commissioning of L.T. floor mounted outdoor Installation, suitable for dust vermin and weather proof construction panel board fabricated out of 14 SWG (2.0mm thick nominal) CRCA M.S. sheet with 40mm x 40mm x 6mm angle iron legs & CRCA MS top cover rain protection canopy as per drawing attached and suitable to accommodate and supplying and fixing the following accessories therein including connections, inter connections with suitable size of copper wire, earth connections, numbering and spray painted after applying a cost of Zinc chromate primer as reqd. - 32 Amps TP&N MCB 10 KA (C Series) –1 No. - 16 Amps TP MCB 10 KA (C Series) – 2 Nos. - DOL Starter with enclosure having suitable relay complete as reqd. –1 No. - Negative sequence current sensing Single phase preventor with dry run & overload protection cum water level guard (cordless) – 1 No. - 3 phase shunt capacitor suitable for Item No.1-1No. - Phase indicator neon lamps with toggle switches and back up fuses –1 Set - Voltmeter 0 to 500 volts 96mm square dial with selector switch – 1 No. - Ammeter 0 to 30 Amps 96 mm square dial – 1 no. - 25 Amp SPN MCB 10 KA ( B series) – 1 No. - 4 strip 300mm long aluminum bus bar 100 amps capacity duly PVC taped / sleeved having drilled holes, 6mm dia bolts, nuts and washers etc. as required – 1 set - Danger notice plate – 1 No. | 2 set |  | Set |  |
| 6. |  | Earthing with G.I. Earth pipe 4.5 mtr long and 40mm dia including accessories and providing masonary enclosure with cover plate having locking arrangement and water pipe etc. (but without salt, charcoal or coke) as reqd. | 4 set |  | Set |  |
| 7 |  | Extra for using salt & charcoal / coke for pipe earth electrode as reqd. | 4 set |  | Set |  |
| 8 |  | Providing & fixing 25mm x 5mm G.I. strip in 40mm dia G.I. pipe from earth electrode as reqd. | 6 mtr. |  | Mtr. |  |
| 9 |  | Providing & Fixing 25mm x 5mm G.I. strip on surface or in recess for earth connections etc. as reqd. | 6 mtr. |  | Mtr. |  |
| 10 |  | Supplying, Laying / Fixing of 40mm dia G.I. pipe B class along with socket, bends etc. in recess / surface as reqd. | 6 mtr. |  | Mtr. |  |
| 11 |  | Supplying of one no. 4 core x 16 sq.mm. XLPE 1.1 KV grade armoured aluminum conductor cable including connections & testing etc. as reqd. | 300 mtr. |  | Mtr. |  |
| 12 |  | Laying of one PVC insulated & PVC sheathed aluminum conductor cable of size not exceeding 25 sq.mm. direct in grounds i/c excavation, sand cushioning, protection covering and refelling the trench etc. as reqd. | 290 mtr. |  | Mtr. |  |
| 13 |  | Laying of one PVC insulated and PVC sheathed aluminum conductor Power cable of size not exceeding 25 sq.mm. in the existing RCC / Hume / Stoneware / Metal Pipe etc. as reqd. | 10 mtr. |  | Mtr. |  |
|  | ### Total |  |  |  |  |  |

## (EXECUTIVE ENGINEER)

Electrical Division – IV/ DDA