NIT No. 11/EE/ED-8/DDA/2008-09		            Estimated cost :- 2,62,977/-

Earnest money :- 5260/-

Date of Sale : 13.06.2008

Date of opening 17.06.2008

DELHI DEVELOPMENT AUTHORITY

ELECTRICAL DIVISION NO. 8/NEW DELHI

SCHEDULE OF WORK

| Name of work | : | M/o Completed scheme of N/A-II under North Zone |
| --- | --- | --- |
| SH | : | R.M.O. of Pumps, fountains & park / path lights installed at Prasad Nagar Lake on annual contract basis. |

| S.No. | Description of items |  | Qty. | Rate | Unit | Amount (Rs.) |
| --- | --- | --- | --- | --- | --- | --- |
| 1. | Maintenance & Operation of Street Lighting, pumps as per Inventory & terms and conditions attached. |  | One job for 12 months |  | P/Month |  |
| 2. | Supplying and replacement of the following items : |  |  |  |  |  |
|  | a) | 125 Watt HPMV lamp | 30 Nos. |  | Each |  |
|  | b) | 150 Watt MHN-T lamp | 6 Nos. |  | Each |  |
|  | c) | 125 Watt HPMV copper wound choke / Ballast | 15 Nos. |  | Each |  |
|  | d) | Choke/Ballast suitable for 150 Watt MHN-T 150 Watt | 6 Nos. |  | Each |  |
|  | e) | Ignitor suitable for 150 Watt MHN-T 150 Watt | 6 Nos. |  | Each |  |
|  | f) | Capacitor 10 MFD | 16 Nos. |  | Each |  |
|  | g) | Capacitor 20 MFD | 6 Nos. |  | Each |  |
| 3. | Painting & Numbering of Steel tubular / G.I. pipe i/c overhangs, connector boxes etc., with double coat of aluminum / enamel paint of approved shade, cleaning the surface etc. as required. |  |  |  |  |  |
|  | a) | 6 mtr. High pole | 27 Nos. |  | Each |  |
|  | b) | 9 mtr. High pole | 2 Nos. |  | Each |  |
| 4. | Spray painting & numbering of feeder pillar with enamel paint of approved shade after cleaning the surface etc. as required. |  | 4 Nos. |  | Each |  |
| 5. | Supply of the following sizes of XLPE armoured / Aluminum conductor power cable of 1.1 KV grade i/c testing connections etc. as required. |  |  |  |  |  |
|  | (i) | 2x16 sq.mm | 60 Mtrs. |  | Mtr. |  |
|  | (ii) | 4x25 sq.mm | 60 Mtrs. |  | Mtr. |  |
| 6. | Laying of one number PVC insulated and PVC sheathed / XLPE armoured power cable of 1.1 KV grade of size not exceeding 25 sq.mm direct in ground i/c excavation and refelling the trench etc. as required but excluding sand cushioning and protective covering. |  | 150 Mtrs. |  | Mtr. |  |
| 7. | Supplying and making straight through joints with cast resin compound including ferrules and other jointing materials for following sizes of PVC insulated and PVC sheathed XLPE armoured aluminum conductor power cable of 1.1 KV grade as required. |  |  |  |  |  |
|  | a) | 4 core x 25 sq.mm | 2 Nos. |  | Each |  |
|  | b) | 2 core x 16 sq.mm | 2 Nos. |  | Each |  |
| 8. | Supplying and Replacement of following types damaged street light fittings with control gear reflector, protection glass cover i/c earthing the body etc. as required. |  |  |  |  |  |
|  | (a) | 125 watt HPMV HID lamp roadway lighting luminaries sheet Al. lamp housing & die cast al. along control gear housing in grey hammer stone stove enameled reflector with acrylic bowl, wire mesh & accessories. | 2 Nos. |  | Each |  |
|  | (b) | 150 watt flood light luminaries with built on control gear model BGEMF 80 MHDE, Bajaj make or equivalent. | 1 |  | Each |  |
| 9. | Supplying & replacement of acrylic sheet cover suitable for 70/125 watt HPMV street light luminaries |  | 15 |  | Each |  |
| 10. | Supplying & replacement of Direct on line starter in sheet steel enclosure suitable for 7.5 HP motor relay range 9-16 Amp, 415V, 3 phase, connections etc. as required. |  | 3 Nos. |  | Each |  |
| 11. | Supplying and installation of motor protection circuit breaker (push button type) suitable for 7.5 KW motor 415 V, with thermal release of 10-16 Ampere as required. |  | 6 Nos. |  | Each |  |

DETAILS OF INVENTORY AT PRASAD NAGAR LAKE

| 1) | Sub-pump sets (3 phase) 415 volts upto 7.5 H.P. | : | 2 Nos. |
| --- | --- | --- | --- |
| 2) | Mono-block sub pump sets (3 phase) – 415 V for fountains upto 10 HP | : | 3 Nos. |
| 3) | Monoblock pump 3 phase upto 10 HP | : | 1 No. |
| 4) | MHNT fitting 150 W | : | 8 Nos. |
| 5) | HPMV lamp fitting 125 W | : | 30 No. |
| 6) | 9 mtr. pole | : | 2 Nos. |
| 7) | 6 mtr. pole | : | 27 Nos. |
| 8) | Feeder Pillar / Pannel | : | 4 Nos. |

ADDITIONAL CONDITIONS & SPECIFICATION

1.	The work shall be carried out as per CPWD specification, 2005 (Int.) and 1994 (Extn.) Part-II.

2.	The work comprises of running, maintenance & operation of pump sets & street lighting as per inventory attached.

3.	Scope of work is “as under :-

(a)	To Keep all street lighting points and allied installations in working order.

(b)	To keep the street lighting functional during the timings fixed by the Engineer-in-charge.

(c)	Street lighting should be switched ON/OFF at appropriate time fixed by the department.

(d)	Running maintenance and, operation submersible Pump Set & its allied installation.

4.	90% of the street lighting should remain in working order & functional throughout the period of contract failing which proportionate recovery shall be made from the contractor’s bill.

5.	No park/path points should remain out of order for more than 3 days.  Beyond 3 days, a recovery of Rs. 50/- per point, per day, shall be made from the contractor’s bill.

6.	For laying of cable and removing of existing damaged/defective cable, payment will be made as per item No. 6 of schedule of work and no extra payment shall be made on this account.

7.	Proper handing / taking over of all the E&M installation, shall be carried out by JE(E)/AE(E) incharge of the work and the contractor’s in writing immediately after award of work and before start of work.  The same shall be handed over to, the department in proper working condition after expiry of the contract.

8.	The contractor shall depute the following staff under the contract.

| (a) | Pump Operator Gd-II |  | 2 No. pump operator one in morning shift and one for evening shift for pump and fountain operation at Prasad Nagar Lake. |
| --- | --- | --- | --- |
| (b) | Wireman Gd-II |  | 1 No. once a week (from 2 p.m to 10 p.m) for maintenance of path / park lighting and its allied installation. |
| (c) | Wireman Gd-I |  | 1 No. twice in a month for maintenance of pump sets & its allied installation. |
| (d) | Khallasi |  | 2 Nos. once in a week (from 2 p.m to 10 p.m) for maintenance of park / path lighting as helper with wire men Gd-II mentioned at 8(b). |

8.	The duty timings of the staff can be changed as and when required by the Engineer-in-Charge.

9.	The contractor shall deploy trained and competent staff to the satisfaction of the Engineer-in-charge.

10.	The contractor shall supply the list of staff along with details i.e. Name, Father’s Name, Date of Birth, Experience Certificate to be engaged on the installation within 7 days of award of work, Engineer-in-charge shall have the right to reject any staff deployed by the contractor.

11.	The staff deployed by the contractor shall wear proper uniform and badges displaying their name and designation.

12.	The contractor shall deploy staff throughout the period of contract as mentioned in additional condition No. 8 and shall maintain attendance register which shall be kept at the office of J.E.(E) concerned.

13.	The contractor shall submit the log sheet as per the performa for each and every park / site enclosed regarding the status of street lighting points and other allied installations of the proceeding day, periodically as per period decided by Engineer-in-charge in the division office, duly signed by him or his authorized representative whose particulars shall be furnished by the successful tenderer within 7 days after award of work.  The contractor shall also keep printed log book at the site of work for recording operation of pumps and complaint / inspection register.  The registers shall be the duly authenticated from Engineer in charge before use at site.

14.	If any staff deployed by the contractor is found absent on a particular time and date, an amount equal to minimum wages fixed by Delhi Administration from time to time shall be recovered from the contractor’s bill.

15.	In case of any Disobedience or misbehavior by the operational staff of the contractor, the Engineer-in-charge may ask the contractor to dispense with the services of such staff with immediate effect. The contractor shall provide suitable substitute simultaneously.

16.	The contractor shall take all safety measures at site during maintenance of the installation.

17.	Any injury/mishap to the maintenance staff during duty hours will solely by the liability of the contractor.

18.	Contractor shall stand guarantee for 12 (Twelve) months from the date of successful completion for the items executed under this contract.

19.	Co-ordination and follow up action with Electric Supply Agency shall be done by the contractor in case of failure / fault in supply.

20.	The contractor shall intimate the Engineer-in-charge about the major breakdown or failure of electric supply immediately.

21.	The following minor maintenance i.e. preventive maintenance shall be carried out by the contractor.  The details of work carried out shall be recorded in the register.

a)	Supplying and replacement of kit kats MCB’s connector, neutral link as when required.

b)	Supplying and replacement of thimbles and ferrules as and when required.

c)	Supplying and replacement of copper wire of size 1.5mm2 & 2.5 MM2 as and when required.

d)	Supplying and replacement of HRC fuses as and when required.

e)	Cable jointing upto 10 sq.mm size of cable.

f)	Adjustment, Alignment/tightening of nuts & bolts as and when required.  Note – The material required for carrying out above job shall be supplied by the contractor within the quoted rates.

22.	All electric connections shall be checked at least, once in a month and set right, if required.

23.	Painting of poles shall be done by using brush or by spray painting.

24.	The contractor has to return the dismantled material to the department after replacing the defective items as site for which separate payments are being made by the department.

25.	All allied accessories / installations shall be kept in working order and in case any damages / loss is done to the installations during the contract period, the contractor shall have to make good the damages / loss at his own cost except the damages to the installations by accident.  In case the contractor fails to rectify the damages/loss within reasonable time, the same shall be got rectified / replaced by the department at the risk and cost of the contractor.

26.	If at any stage, the timer switch provided in the feeder pillar does not function that ON/OFF operation shall be done manually till the timer switch is got repaired/replaced.  Nothing extra shall be paid on this account.

27.	Items at Sl. No. 2,5,6 & 7, shall be executed as and when required and these shall be executed in the presence of authorized representative of the Engineer-in-charge.  However, all material brought at site, before use shall be got approved from Engineer in charge and 50% of stipulated qty. of material I.r.o. item No. 2 shall be handed over to deptt. immediately & same) be issued by JE(E) incharge for fixing at site as & when required.

28.	The following makes of the materials are acceptable.

a)	Lamps		Philips / Osram

b)	Ballast		As per fitment of manufacturer of existing luminaire.

c)	Ignitor 		As per fitment of manufacturer of existing luminaire.

d)	MCBs 		Legrand/Standard/Action/L&T/Indokopp

e)	Copper wire		National / Ecko / Havelles / Skytone (ISI marked to

IS : 694)

f)	Paint Enamel / Aluminum – Berger / Nerolac/Aisan / Dulux

g)	XLPE Armoured cable Asian Cable /Unistar/Ecko/Nicco/Skytone

(ISI marked to IS : 7098)

h)	Starter / accessories L&T/Siemens/Cutler Hammer/Bentex

29.	The contractor shall also be responsible for removal of unauthorized hoardings, banners, if any, on the poles during the contract period for which the Engineer-in-charge/Authorized representative shall render their assistance, if required.

30.	Testing of earth continuity and earth electrodes shall be carried out once in a year by the contractor in the presence of authorized representative of the Engineer-in-charge.

31.	The rates quoted by the contractor shall be inclusive of all taxes, duties and Govt. levies etc.

32.	The Engineer-in-Charge if so desire, may extend the contract upto 2 months or terminate the contract at any time after giving 15 days notice for which no compensation shall be paid.

33.	Watch and Ward of the Installation during operating hours and during the period while carrying out maintenance shall be the responsibility of the contractor.  Any loss due to the theft or pilferage during the above timings shall be the responsibility of the contractor.

34.	The payment, to the contractor shall be made bi-monthly or at other suitable intervals as desired by the contractor but not less than one month.

35.	The, contractor shall arrange all necessary spares and T&P required for operation & maintenance to be carried out under this contract.

36.	The contractor shall erect the overhead cable within the quoted rates & nothing extra shall be paid on this A/c.

37.	No T&P shall be issued to the contractor by the department.

ANNEXURE-A

SCHEDULE OF PREVENTIVE MAINTENANCE

(For Submersible P/Sets)

| S.No. | Description | Period |
| --- | --- | --- |
| 1. | Cleaning of light fittings, feeder pillars, electric control, panel boards & other accessories. | Fortnightly |
| 2. | Checking of starter contact, relays, timers, push buttons, single phase preventors of pump starters, PVC wire leads, nuts & bolts, main switches, fuses, indication lamps and gaskets provided on the doors of different compartment of feeder pillars, electric control panel boards, gaskets, stoppers & nuts and bolts of piping & its accessories, tightening of all electrical connection, decarbonising of starter contacts and switch gears including supplying and replacement if found defective or worm out parts. | Fortnightly |
| 3. | Rectifying of leakages of valves and accessories i.e. flanges, sockets & bends | Fortnightly |
| 4. | Greasing of sluice valves etc. | Monthly |
| 5. | Insulation and earth tests. | Yearly |
| 6. | Cleaning and Flushing of sump, adjustment of nozzles, fountain lights etc. (For fountain, installation only) | Fortnightly |