NOTICE NO. 9 /EE/ED-7/DDA/07-08

N.I.T.NO.25

SCHEDULE OF WORK

NAME OF WORK : M/o pump sets at various places under North Zone.

SUB HEAD		:- R/M/O of submersible pump set booster pump set and DG set 30 			KVA for 660 LIG incremental hoses in sector A-6 Pkt, I Narela.

| S.No. | Description of items | Qty. | Unit | Rate. | Amount |
| --- | --- | --- | --- | --- | --- |
| 1. | Operation of pumps /DG set as per the inventory and terms and conditions attached | 12 month | Month |  |  |
| 2. | Supply & replacement of the following items - HPSV lamp 70 watt.(E) - Copper wound polyster filled ballast 70 watt. | 2Nos. 2 Nos. | Each Each |  |  |

INVENTORY

PART –A

- Booster pumps

(a) 20 HP centrifugal pump seat 					2 Nos.

(b)  0.5 HP Vacuum pump for priming of above pump set	1 Nos.

(c) Control panel comprising of main switch 125 amp. 63 amp, MCB 4 pole

(d) Details of valves 8 Nos.

PART-B

- D.G. Set

- Capacity 30 KVA 1 No.

- Control panel comprising MCB, Voltmeter , Amp.

PART-C

- Submersible  pumps

- 7.5 HP submersible pump set

- control panel comprising of starter MCB

PART-D

(i) Water level indicator 	1No.

PART-E

- Internal Electrical installation 5 Nos. tube fitting .

- External Electrical installation 4 Nos. HPSV 70 watt.

(compound lighting etc)

TERMS AND CONDITIONS

The work comprises of running and operation of pump sets D.G set and general lighting as per the inventory attached

The contractor shall depute the following staff under the contract.

  - Operator – 2 Nos. one in each shift i.e. from 6.00A.M to 2.00 P.M. and from 2.00P.M. to 10.00 P.M.

  - Khallasi – 1 No. from 10.00 P.M. to 6.00 P.M.

  - Wire man Grade – I shall attend the site of work between 9.00 A.M. to 5.00 P.M. at least once in a fortnight  and as and when required

The contractor shall employ trained and competent staff to the satisfaction of Engineer in charge having two years experience on operation of pump /D.G set.

The contractor shall supply the list of staff along with experience certificates to be engaged on the installation within 7 days of award of work. Engineer in charge shall have the right to reject any staff employed by the contractor.

The staff employed by the contractor shall wear proper uniform and wear badges displaying by their name and designation. The staff shall also be given photo identity cards by the contractor displaying their name,  father name, date of birth name of agency with address and telephone No. site for which employed and period of validity. A copy of the identity cards shall be given to the Engineer in charge within 15 days of award of work.

The contractor shall employ staff throughout the period of contract including Saturdays, Sunday, Gazetted holidays and National holidays.

Following records are to be kept at site of work.

  - printed log book for recording operation

  - attendance register for staff deployed

  - complaint / Inspection register

Note:- The contractor shall get the registers authenticated from Engineer in charge before use at site.

Following minor maintenance including preventive maintenance shall be carried out by the contractor. The details of work carried out shall be recorded in the log book.

- Servicing and greasing of pumps / motors once in 3 months

- Replacement of rubber packing of valves and worn out nuts and bolts etc.

- Replacement of gland dori as and when required

- Replacement of HRC fuses as and when required.

- Replacement of FI Tubes, incandescent lamps and starters.

- Adjustment, alignment/ tightening of nuts and bolts as sans when required.

- Replacement of burnt out thimbles, wire terminals etc.

- Top up of battery water

- Daily cleaning of equipments / pump house.

Note :- The material required for carrying out above jobs shall be supplied by the contractor within quoted rates.

The D.G set shall be operated in case of electricity failure or as and when desired by the Engineer in charge.  However P.O.L shall be supplied by the department.

Co-ordination and follow up action with electric supply agency shall be done by the contractor in case of failure / fault in supply / fluctuation in voltage.

The contractor shall intimate the Engineer in charge about the major breakdown or failure of electric supply in time.

Watch and ward shall be the responsibility of the contractor. Any loss due to theft or pilferage etc. shall be borne by the contractor.

The payment to the contractor shall be made bi- monthly or at other suitable intervals desired by the contractor but not less than one calendar month.

Proper handing /taking over of all the E& M installations shall be carried out by JE(E) in charge of the work and the contractor in writing immediately after award of work / before start of work.

The Engineer in charge if so desire may extend the contract upto2 months or terminate the contract at any time after giving 15 days notice.

If may staff employed by the contractor is found absent on a particular time and date an amount proportionate to per shift shall be recovered from the contractor’s bill

All allied accessories / installations shall be kept in working order and in case any damages / loss is done t the pumping installations due to the negligence of the operational staff deployed by the contractor the contractor shall have to make good the damages / loss at his own cost. In   case the contractor fails to rectify the damages / loss within reasonable time, the same shall be got rectified, replaced by the department at the risk and cost of the contractor

The contractor shall keep all the necessary spares and T& P at site required for operation and maintenance to be carried under his contract.

In case of any disobedience or misbehavior by the operational staff of the contractor the Engineer in charge may ask the contractor to dispense with the serviced of such staff with immediate effect. The contractor shall provide suitable substitute-  simultaneously.

The rates quoted by the contractor shall be inclusive of all taxes duties and Govt. levies etc.

Pumping installation shall be painted (excluding control panel) once during the contract period.

Any injury to the operational staff in case of any mishap, during duty hours will be the liability of contractor.

Testing of earth continuity and earth electodes shall be carried out once in a year by the contractor in the presence of authorized representative of the Engineer in charge.

The following makes of the materials are acceptable

a) HPSV lamp.		Phillips /  Osram.

b) Ballast:			As per fitment of manufacturer of existing luminair.