## SCHEDULE OF QUANTITIES
DELHI DEVELOPMENT AUTHORITY
Name of work: C/o 1811 DU’s (947 HIG, 504 MIG & 360 LIG) in Sector-18B, Dwarka Ph-II i/c internal development of land, Electrical work, Street light & Horticultural Works SH:- SITC of Panel, Feeder Pillar, Cables & Cable Trays etc for Pocket-I.
SCHEDULE OF QUANTITIES NIT No.:- SE(E)-I/DWK/NIT-07/2012-13 Estimated Cost: Rs.33,70,975
S. No. | Description of Item | Qty | Unit | Rate | Rate in words | Amount
1 | Supplying, installation, testing & commissioning of floor mounted, LT cubical feeder pillar outdoor free standing type duly compartmentalized made out of 2 mm thick M.S. CRCA sheet, powder coated paint making connection, interconnection of the accessories mounted thereon with suitable size of copper wire / strip with thimble / lugs, earthing the body of the feeder pillar, i/c suitable size of foundation etc. complete as required. i/c supplying and fixing of following items & as per additional conditions, technical specifications & drawing enclosed. | 3 | Set |  | #VALUE! | 0
A) | Incoming |  |  |  | #VALUE! | 0
a) | 250 Amp MCCB, 4 Pole, 415 V with Thermal magnetic release having breaking capacity 35 KA - 1No. |  |  |  | #VALUE! | 0
b) | Ammeter 0-250A with Selector Switch, size 96 mm x 96 mm --- 1 No. |  |  |  | #VALUE! | 0
[5 empty] | #VALUE! | 0
c ) | C-T's Ratio 250 / 5A, CL-1.0 - 3Nos. |  |  |  | #VALUE! | 0
d) | Voltmeter 0- 500V with Selector Switch -1 No. |  |  |  | #VALUE! | 0
e) | Phase indicator lamp (R.Y.B.) -1 Set |  |  |  | #VALUE! | 0
f) | 6 Amp SP MCB, 10 KA breaking capacity - 3 Nos. |  |  |  | #VALUE! | 0
g) | Danger notice plate of 200 mm x150 mm made of mild steel at least 2 mm thick - 2 Nos. |  |  |  | #VALUE! | 0
B) | Bus Section |  |  |  | #VALUE! | 0
a) | 4 x 300 Amp Capacity aluminum bus bars duly coloured sleeve i/c supports etc. complete as required. |  |  |  | #VALUE! | 0
c ) | Outgoing |  |  |  | #VALUE! | 0
a) | 125 Amp MCCB, 4 pole , 415 V with Thermal magnetic release having breaking capacity 35 KA -5 Nos. |  |  |  | #VALUE! | 0
b) | 63 Amp 4 Pole MCB, 10 KA breaking capacity -1 No. |  |  |  | #VALUE! | 0
c ) | 32Amp 4 Pole MCB, 10 KA breaking capacity - 2 Nos. |  |  |  | #VALUE! | 0
d) | 16 Amp 4 pole MCB 10 KA breaking capacity - 1 No. |  |  |  | #VALUE! | 0
e) | 32 Amp 2 pole MCB 10 KA, breaking capacity -2 Nos. |  |  |  | #VALUE! | 0
2 | Supplying, installation, testing & commissioning of floor / wall mounted, LT cubical Panel board indoor type, duly compartmentalized made out of 2 mm thick M.S. CRCA sheet, powder coated paint making connection, interconnection of the accessories mounted thereon with suitable size of copper wire / strip with thimble / lugs, earthing the body of the Panel board complete as required. i/c supplying and fixing of following items & as per additional conditions, technical specifications . | 1 | Set |  | #VALUE! | 0
A) | Incoming |  |  |  | #VALUE! | 0
a) | 250 Amp MCCB, 4 Pole, 415 V, Thermal magnetic release with breaking capacity 35 KA - 1No. |  |  |  | #VALUE! | 0
b) | Ammeter 0-250 A with Selector Switch, Size 96 mm x 96mm |  |  |  | #VALUE! | 0
c ) | C-T's Ratio 250/ 5A, CL-1.0 - 3Nos |  |  |  | #VALUE! | 0
d) | Voltmeter 0- 500V with Selector Switch -1 No. |  |  |  | #VALUE! | 0
e) | Phase indicator lamp (R.Y.B.) - 1 Set |  |  |  | #VALUE! | 0
f) | 6 Amp. SP MCB 10 KA, breaking capacity - 3 Nos. |  |  |  | #VALUE! | 0
g) | Danger notice plate of 200 mm x150 mm made of mild steel at least 2 mm thick - 2 Nos. |  |  |  | #VALUE! | 0
#VALUE!
b) | Bus Section |  |  |  | #VALUE! | 0
a) | 4 x 300 Amp Capacity aluminum bus bars duly coloured sleeve i/c supports etc. complete as required. |  |  |  | #VALUE! | 0
C ) | Outgoing |  |  |  | #VALUE!
a) | 200 Amp MCCB, 4 pole , 415 V, Thermal magnetic release with breaking capacity 35 KA -1 No. |  |  |  | #VALUE! | 0
b) | 32 Amp 4 Pole, MCB, 10 KA, breaking capacity – 3 Nos. |  |  |  | #VALUE! | 0
c ) | 16 Amp 2 pole MCB ,10 KA, breaking capacity - 3 Nos. |  |  |  | #VALUE! | 0
3 | Providing & fixing following rating and breaking capacity MCCB in the suitable size sheet steel enclosure painted with powder coated i/c drilling holes making connection earthing etc. as required. |  |  |  | #VALUE! | 0
a) | 250 Amp 4 pole MCCB, 415 V, Thermal magnetic release with breaking capacity 35 KA -1 No. | 3 | EACH |  | #VALUE! | 0
b) | 32 Amp 4 pole MCCB, 415 V with thermal magnetic release with breaking capacity 16 KA – 1 No. | 15 | EACH |  | #VALUE! | 0
4 | Fabricating & Installation following size of perforated M.S. cable trays including Horizontal and vertical bends, reducers ,tees, cross members and other accessories as required and duly suspended from the ceiling with M.S. suspenders & i/c painting with powder coating etc as required. |  |  |  | #VALUE!
a) | 900 mm. width x 75mm depth x 2.00 mm. thickness | 150 | mtrs. |  | #VALUE! | 0
b) | 750 mm. width x 75mm depth x 2.00 mm. thickness | 40 | mtrs. |  | #VALUE! | 0
c ) | 600 mm. width x 75mm depth x 2.00 mm. thickness. | 300 | mtrs. |  | #VALUE! | 0
d) | 450 mm. width x 50mm depth x 2.00 mm. thickness | 200 | mtrs. |  | #VALUE! | 0
e) | 300 mm. width x 50 mm depth x 1.6 mm. thickness | 100 | mtrs. |  | #VALUE! | 0
f) | 100 mm. width x 50 mm depth x 1.6 mm. thickness | 20 | mtrs. |  | #VALUE! | 0
g) | 150 mm. width x 50 mm depth x 1.6 mm. thickness | 400 | mtrs. |  | #VALUE! | 0
| Cables - |  |  |  | #VALUE!
5 | Supplying of the following sizes of XLPE insulated PVC sheathed Aluminium conductor armoured power cable of 1.1KV grade including connection, testing etc. as reqd. |  |  |  | #VALUE!
i) | 3.5 C x 185 sq. mm. | 600 | mtrs. |  | #VALUE! | 0
ii) | 4 C x 50 sq.mm. | 1400 | mtrs. |  | #VALUE! | 0
iii) | 4 C x 25 sq. mm. | 450 | mtrs. |  | #VALUE! | 0
iv) | 2 C x 25 sq. mm. | 200 | mtrs. |  | #VALUE! | 0
6 | Supplying and making end termination with brass compression gland & Al. lugs for following size of PVC insulated & PVC sheathed / XLPE aluminium cond. Cable of 1.1 KV grade etc as required. |  |  |  | #VALUE!
a) | 3.5 C x185 sq. mm. | 9 | EACH |  | #VALUE! | 0
b) | 4 C x 50 sq. mm. | 30 | EACH |  | #VALUE! | 0
c ) | 4 C x 25 sq. mm. | 20 | EACH |  | #VALUE! | 0
d) | 2 C x 25 sq mm. | 10 | EACH |  | #VALUE! | 0
7 | Laying & fixing of one No. PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade of size not exceeding 25 sq. mm. on surface as required. |  |  |  | #VALUE! | 0
a) | 2 C x 25 sq. mm. | 175 | mtrs. |  | #VALUE! | 0
b) | 4 C x 25 sq. mm. | 425 | mtrs. |  | #VALUE! | 0
8 | Laying & fixing of one No. PVC insulated and PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade of size exceeding 25 sq. mm. but not exceeding 120 sq. mm on surface as required. |  |  |  | #VALUE! | 0
a) | 4C x 50 Sq mm. | 1200 | mtrs. |  | #VALUE! | 0
9 | Laying & fixing of one No. PVC insulated & PVC sheathed / XLPE aluminium conductor cable of 1.1 KV grade of size exceeding 120 sq. mm but not exceeding 400 Sq mm on surface as required. |  |  |  | #VALUE! | 0
a) | 3.5 C x 185 Sq mm. | 200 | mtrs. |  | #VALUE! | 0
10 | Laying of 1 No. PVC Insulated & PVC Sheathed / XLPE Power cable of 1.1 KV Gr. of size not exceeding 25 sq. mm. in existing R.C.C. /Hume/ Stoneware/ metal / DWC pipe as required. |  |  |  | #VALUE! | 0
a) | 4C x 25 sq. mm. | 25 | mtrs. |  | #VALUE! | 0
b) | 2C x 25 sq. mm. | 25 | mtrs. |  | #VALUE! | 0
11 | Laying of 1 No. PVC Insulated & PVC Sheathed / XLPE Power cable of 1.1 KV Gr. of size exceeding 25 sq. mm but not exceeding 400 sq. mm. in existing R.C.C. /Hume/ Stoneware/ metal / DWC pipe as required. |  |  |  | #VALUE! | 0
a) | 4 C x 50 sq. mm. | 200 | mtrs. |  | #VALUE! | 0
b) | 3.5 C x 185 sq. mm. | 400 | mtrs. |  | #VALUE! | 0
12 | Earthing with G.I. Earth pipe 4.5 mtr long, 40mm dia including accessories and providing masonary enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal and salt as reqd. | 6 | Sets |  | #VALUE! | 0
13 | Providing & fixing 25mm x 5mm GI strip in 40 mm dia G.I. pipe from earth electrode, as required. | 30 | mtrs. |  | #VALUE! | 0
14 | Providing & Fixing of 25mm x 5mm GI strip on surface or in recess for connection etc. as reqd. | 30 | mtrs. |  | #VALUE! | 0
0